Weott CSD’s Operator’s Report
09-10-2026 
Greg Teasley & Curren Black

Springs/Flow: 
Curren and I crossed the river and went up to B-sides spring, to find a very low flow of water that is even available to catch, but we were able to increase the flow by roughly 5 to 10 gpm.
The settling tank for B side is settling into the ground which is causing a lot of stress on the clean out pipes on the bottom of the tank. One of them is already leaking. But as old as the tank is, we don't dare touch it for fear of causing more damage.
We are planning to go to the A source soon, but we are still getting good flow on that side.  We will have to go over to clean out all the debris that falls off the trees at this time of year.

Test Results: 
Water quality has been passing state standards.
    
Water Plant:  
It has been working efficiently.

Wastewater Plant: 
It is passing tests and there are no new malfunctions. 

Lift station: 
Both pumps are working as they should 

Repairs & Leaks                                                                                                                                                 The leak on south spring street has been repaired.                                                                                  I found and repaired a big leak on the service line to the state park campground in lower Weott…    redwood roots had compromised the polypipe and popped a hole in it.
Curren and I have dug up to the foot of the embankment on the west side of the freeway, trying to locate the leak. But as saturated as the ground is, we're thinking that it's probably further back under the off ramp. This part of A line under the freeway only serves two houses on Spur st. The B line on lum street I measured, is 250 feet away.
The two leaks on Newton road- One of them is by School road and they are definitely treated water. Both of them will need to be repaired. We will need flaggers or at least one because the asphalt road surface will need to be dug up and traffic will need to be directed while the repair is being made.  I can't tell if the leak by School road is just one valve leaking or both. But I'm pretty sure that those are at least 4 if not 6 inch valves that might need to be replaced.

       
        


